## Technology Parameters
| HP | BAT | PCM |  | WG | PV
max kW / module | 50 | 82 | 50 | Capital cost | 2500 | 2000
max kWh (=100%Soc) / module | 286.125 | 82 | 205 | O&M cost Euro/kWh | 0.012 | 0.01
O&M cost/kWh | 0.0011 | 0.002 | 0.003
O&M cost / module | 0.31474 | 0.164 | 0.615
Specific capital cost/kWh | 200 | 350 | 83
Specific capital cost/modul | 57225 | 28700 | 17015
Hipothesys
HP
Plant power: | 450 | kW
Plant efficiency: | 0.75
Pumping power: | 600 | kW
Stored energy: | 2575 | kWh
Discharge time: just over | 5 | hours
Charge time: | 6 | hours
O&M | 11 | c€/kWh
BATTERY
Plant power: | 6806 | kW
Plant efficiency: | over 95%
Stored energy: | 6806 | kWh
Discharge time: just over | 1 | hour
Charge time: | 1 | hour
O&M | 0.2 | c€/kWh
SCENARIO SELF CONSUMPTION |  |  | The self-consumption scenario means that we minimize the energy drawn from the grid. |  |  |  | KPI= | total energy buy fom the grid for the considered scenario (i.e., 51th day)/ total energy bought from the distribution grid scenario base
SCENARIO ECO OBJ |  |  | The eco -bj scenario means that we minimize the total energy costs |  |  |  | KPI = | OBJ FUNCTION VALUE for the considered scenario / OBJ FUNCTION VALUE SCENARIO BASE
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I have changed this values

## Scenario
[5 empty] | Total maximum power |  |  | Total capacity of ESS
| NESS_HP | NESS_BAT | NESS_PCM | Total capital cost of storage | HP (kW) | BAT (kW) | PCM (kW) | HP (kWh) | BAT (kWh) | PCM (kWh) | Total O&M cost of storage
Scenario_Base_1 | 9 | 83 | 28 | 3373545 | 450 | 6806 | 1400 | 2575.125 | 6806 | 5740 | 56.4002
Scenario_Base_2 | 9 | 88 | 20 | 3380925 | 450 | 7216 | 1000 | 2575.125 | 7216 | 4100 | 53.5303
Scenario_Base_3 | 9 | 78 | 36 | 3366165 | 450 | 6396 | 1800 | 2575.125 | 6396 | 7380 | 59.2703
Scenario_UpperCost_1 | 9 | 90 | 36 | 3710565 | 450 | 7380 | 1800 | 2575.125 | 7380 | 7380 | 64.1903
Scenario_UpperCost_2 | 9 | 95 | 28 | 3717945 | 450 | 7790 | 1400 | 2575.125 | 7790 | 5740 | 61.3203
Scenario_UpperCost_3 | 9 | 85 | 44 | 3703185 | 450 | 6970 | 2200 | 2575.125 | 6970 | 9020 | 67.0602
Scenario_LowerCost_1 | 9 | 75 | 22 | 3041855 | 450 | 6150 | 1100 | 2575.125 | 6150 | 4510 | 49.4303
Scenario_LowerCost_2 | 9 | 80 | 13 | 3032220 | 450 | 6560 | 650 | 2575.125 | 6560 | 2665 | 45.9453
Scenario_LowerCost_3 | 9 | 70 | 30 | 3034475 | 450 | 5740 | 1500 | 2575.125 | 5740 | 6150 | 52.3003
Scenario_Base_1 |  | 0 | 0
Scenario_Base_2 |  | 5 | -8
Scenario_Base_3 |  | -5 | 8
Scenario_UpperCost_1 |  | 7 | 8
Scenario_UpperCost_2 |  | 12 | 0
Scenario_UpperCost_3 |  | 2 | 16
Scenario_LowerCost_1 |  | -8 | -6
Scenario_LowerCost_2 |  | -3 | -15
Scenario_LowerCost_3 |  | -13 | 2
Same Capital Cost
10% investment increase
10% investment decrease

## DAY 51th_ECO_OBJ_BASE1
| ELEC_PRIC | EL | HP | BATT | EL_GRID | THERMAL LOAD | PCM | BOILER | 0.25714 | 0.25443 | 0.25298 | 0.25275 | 0.25498 | 0.20627 | 0.26978 | 0.27708 | 0.27673 | 0.27678 | 0.27037 | 0.2669 | 0.26475 | 0.26649 | 0.27007 | 0.27432 | 0.27111 | 0.28213 | 0.2809 | 0.27616 | 0.27117 | 0.06649 | 0.061108
1 | 0.26039 | 391.7357 | 337.5 | 3400 | 0 | 62.75 | 0 | 62.75
2 | 0.25714 | 395.1273 | 337.5 | 3400 | 732.6273 | 62.75 | 0 | 62.75
3 | 0.25443 | 386.8388 | 337.5 | 3400 | 724.3388 | 62.75 | 0 | 62.75
4 | 0.25298 | 400.3276 | 337.5 | 4400 | 1737.8276 | 62.75 | 0 | 62.75
5 | 0.25275 | 398.2891 | 337.5 | 5800 | 1735.7891 | 62.75 | 0 | 62.75
6 | 0.25498 | 485.7462 | 337.5 | 6800 | 1823.2462 | 89.093 | 5740 | 0
7 | 0.26271 | 487.6569 | 337.5 | 5974.8431 | 0 | 608.3333 | 5131.6667 | 0
8 | 0.26978 | 514.6485 | -337.5 | 5797.6945 | 0 | 1032.7789 | 4098.8877 | 0
9 | 0.27708 | 272.8647 | -337.5 | 5862.3299 | 0 | 1047.9167 | 3050.971 | 0
10 | 0.27673 | -477.4913 | -212.625 | 5862.3299 | -690.1163 | 857.7355 | 2193.2355 | 0
11 | 0.27678 | -1103.9603 | 0 | 6800 | -166 | 744.0641 | 1449.1714 | 0
12 | 0.27037 | -725.2451 | 0 | 6800 | -725.2451 | 763.9758 | 685.1957 | 0
13 | 0.2669 | -860.6872 | 0 | 6800 | -860.6872 | 718.9807 | 0 | 33.8
14 | 0.26475 | -423.8448 | 0 | 6800 | -423.8448 | 719.5689 | 1260 | 719.56
15 | 0.26649 | -910.6803 | 0 | 6800 | -910.6803 | 694.4022 | 2520 | 694.4
16 | 0.27007 | -930.26 | 0 | 6800 | -930.26 | 720.157 | 1799.843 | 0
17 | 0.27432 | -999.7032 | 0 | 6800 | -999.7032 | 765.2354 | 1034.6076 | 0
18 | 0.27111 | -114.5188 | 0 | 6800 | -114.5188 | 745.3237 | 289.2838 | 0
19 | 0.28213 | 337.5168 | -337.5 | 4761 | -2039 | 475.8719 | 1549.2838 | 475.8719
20 | 0.2809 | 465.6 | -337.5 | 4632.9 | 0 | 601.4552 | 947.8286 | 0
21 | 0.27616 | 512.742 | -337.5 | 4457.6579 | 0 | 491.0096 | 456.819 | 0
22 | 0.27117 | 508.746 | -337.5 | 4286.4119 | 0 | 296.343 | 160.476 | 0
23 | 0.26649 | 510.5492 | -337.5 | 4113.3627 | 0 | 151.9263 | 8.5497 | 0
24 | 0.26111 | 500.7015 | 212.625 | 3400.0362 | 0 | 32.0048 | 0 | 23.4
0

## DAY 51th_SELFCONSUMPTION_BASE
| PRIC EL | PRICE_GAS [c€/m3] | EL LOAD | HP | BATT | GRID | TH LOAD | PCM | BOILER | P_battery | P_PCM | El_mismatch | Th Mismatch | 0.25714 | 0.25443 | 0.25298 | 0.25275 | 0.25498 | 0.20627 | 0.26978 | 0.27708 | 0.27673 | 0.27678 | 0.27037 | 0.2669 | 0.26475 | 0.26649 | 0.27007 | 0.27432 | 0.27111 | 0.28213 | 0.2809 | 0.27616 | 0.27117 | 0.06649 | 0.061108
1 | 0.26039 | 0.53 | 391.7357 | 337.5 | 3400 | 0 | 62.75 | 0 | 62.75 | 0 | 0 | 729.2357 | 0
2 | 0.25714 | 0.53 | 395.1273 | 337.5 | 2667.3727 | 0 | 62.75 | 0 | 62.75 | -732.6273 | 0 | 1.1369e-13 | 0
3 | 0.25443 | 0.53 | 386.8388 | 337.5 | 1943.0339 | 0 | 62.75 | 0 | 62.75 | -724.3388 | 0 | -2.2737e-13 | 0
4 | 0.25298 | 0.53 | 400.3276 | 337.5 | 1205.2063 | 0 | 62.75 | 0 | 62.75 | -737.8276 | 0 | 0 | 0
5 | 0.25275 | 0.53 | 398.2891 | 337.5 | 469.4173 | 0 | 62.75 | 0 | 62.75 | -735.7891 | 0 | 0 | 0
6 | 0.25498 | 0.53 | 485.7462 | 337.5 | 0 | 354 | 89.093 | 5740 | 0 | -469.4173 | -62.75 | 707.8289 | -151.843
7 | 0.26271 | 0.53 | 487.6569 | 337.5 | 0 | 150.1569 | 608.3333 | 5131.6667 | 0 | 0 | 0 | 975.3139 | -608.3333
8 | 0.26978 | 0.53 | 514.6485 | -337.5 | 0 | 177.1485 | 1032.7789 | 4098.8877 | 0 | 0 | 0 | 354.2971 | -1032.7789
9 | 0.27708 | 0.53 | 272.8647 | -337.5 | 64.63 | 0 | 1047.9167 | 3050.971 | 0 | 64.63 | 0 | -0.005334 | -1047.9167
10 | 0.27673 | 0.53 | -477.4913 | -212.625 | 754.7463 | 0 | 857.7355 | 2193.2355 | 0 | 690.1163 | 0 | 0 | -857.7355
11 | 0.27678 | 0.53 | -1103.9603 | 0 | 1858.7066 | 0 | 744.0641 | 1449.1714 | 0 | 1103.9603 | 0 | 2.2737e-13 | -744.0641
12 | 0.27037 | 0.53 | -725.2451 | 0 | 2583.9517 | 0 | 763.9758 | 685.1957 | 0 | 725.2451 | 0 | -1.1369e-13 | -763.9758
13 | 0.2669 | 0.53 | -860.6872 | 0 | 3444.6388 | 0 | 718.9807 | 0 | 33.8 | 860.6872 | 33.8 | 1.1369e-13 | -651.3807
14 | 0.26475 | 0.53 | -423.8448 | 0 | 3868.4836 | 0 | 719.5689 | 1260 | 719.56 | 423.8448 | 685.76 | 1.1369e-13 | 685.7511
15 | 0.26649 | 0.53 | -910.6803 | 0 | 4779.164 | 0 | 0 | 2520 | 694.4 | 910.6803 | -25.16 | 2.2737e-13 | 669.24
16 | 0.27007 | 0.53 | -930.26 | 0 | 5709.424 | 0 | 720.157 | 1799.843 | 0 | 930.26 | -694.4 | 4.5475e-13 | -1414.557
17 | 0.27432 | 0.53 | -999.7032 | 0 | 6709.1271 | 0 | 765.2354 | 1034.6076 | 0 | 999.7032 | 0 | -1.1369e-13 | -765.2354
18 | 0.27111 | 0.53 | -114.5188 | 0 | 6806 | 17.8 | 745.3237 | 289.2838 | 0 | 96.8729 | 0 | 0.15409 | -745.3237
19 | 0.28213 | 0.53 | 337.5168 | -337.5 | 6806 | 17.7 | 475.8719 | 1549.2838 | 475.8719 | 0 | 475.8719 | 17.7168 | 475.8719
20 | 0.2809 | 0.53 | 465.6 | -337.5 | 3400 | -3295.5 | 601.4552 | 947.8286 | 0 | -3406 | -475.8719 | -6573.4 | -1077.3271
21 | 0.27616 | 0.53 | 512.742 | -337.5 | 3400 | 175.242 | 491.0096 | 456.819 | 0 | 0 | 0 | 350.4841 | -491.0096
22 | 0.27117 | 0.53 | 508.746 | -337.5 | 3400 | 171.246 | 296.343 | 160.476 | 0 | 0 | 0 | 342.4921 | -296.343
23 | 0.26649 | 0.53 | 510.5492 | -337.5 | 3400 | 173.0492 | 151.9263 | 8.5497 | 0 | 0 | 0 | 346.0984 | -151.9263
24 | 0.26111 | 0.53 | 500.7015 | 212.625 | 3400 | 713.3265 | 32.0048 | 0 | 23.4 | 0 | 23.4 | 1426.653 | 14.7952
0

## DAY 51th_SELFCONSUMPTION_BA (3)
| PRIC EL | PRICE_GAS [c€/m3] | EL LOAD | HP | BATT | GRID | THERMAL LOAD | PCM | BOILER | 0.25714 | 0.25443 | 0.25298 | 0.25275 | 0.25498 | 0.20627 | 0.26978 | 0.27708 | 0.27673 | 0.27678 | 0.27037 | 0.2669 | 0.26475 | 0.26649 | 0.27007 | 0.27432 | 0.27111 | 0.28213 | 0.2809 | 0.27616 | 0.27117 | 0.06649 | 0.061108
1 | 0.26039 | 0.53 | 391.7357 | 337.5 | 3200 | 0 | 62.75 | 791.476 | 62.75
2 | 0.25714 | 0.53 | 395.1273 | 337.5 | 2467.3727 | 0 | 62.75 | 2271.476 | 62.75
3 | 0.25443 | 0.53 | 386.8388 | 337.5 | 1743.0339 | 0 | 62.75 | 4542.952 | 62.75
4 | 0.25298 | 0.53 | 400.3276 | 337.5 | 1005.2063 | 0 | 62.75 | 6814.428 | 62.75
5 | 0.25275 | 0.53 | 398.2891 | 337.5 | 269.4173 | 0 | 62.75 | 7380 | 62.75
6 | 0.25498 | 0.53 | 485.7462 | 337.5 | 0 | 553 | 89.093 | 7290.907 | 0
7 | 0.26271 | 0.53 | 487.6569 | 337.5 | 0 | 1378.1569 | 608.3333 | 6682.5737 | 0
8 | 0.26978 | 0.53 | 514.6485 | -337.5 | 0 | 177.1485 | 1032.7789 | 5649.7947 | 0
9 | 0.27708 | 0.53 | 272.8647 | -337.5 | 64.63 | 0 | 1047.9167 | 4601.8781 | 0
10 | 0.27673 | 0.53 | -477.4913 | -212.625 | 754.7463 | 0 | 857.7355 | 3744.1425 | 0
11 | 0.27678 | 0.53 | -1103.9603 | 0 | 1858.7066 | 0 | 744.0641 | 3000.0785 | 0
12 | 0.27037 | 0.53 | -725.2451 | 0 | 2583.9517 | 0 | 763.9758 | 2236.1027 | 0
13 | 0.2669 | 0.53 | -860.6872 | 0 | 3444.6388 | 0 | 718.9807 | 1517.122 | 0
14 | 0.26475 | 0.53 | -423.8448 | 0 | 3868.4836 | 0 | 719.5689 | 797.5531 | 0
15 | 0.26649 | 0.53 | -910.6803 | 0 | 4779.164 | 0 | 694.4022 | 103.1509 | 0
16 | 0.27007 | 0.53 | -930.26 | 0 | 5709.424 | 0 | 720.157 | 0 | 617
17 | 0.27432 | 0.53 | -999.7032 | 0 | 6396 | 313.2 | 765.2354 | 1480 | 765.2354
18 | 0.27111 | 0.53 | -114.5188 | 0 | 6396 | -114.5188 | 745.3237 | 2960 | 745.3237
19 | 0.28213 | 0.53 | 337.5168 | -337.5 | 6396 | 0 | 475.8719 | 2484.1281 | 0
20 | 0.2809 | 0.53 | 465.6 | -337.5 | 5100 | 1167.9 | 601.4552 | 1882.6729 | 0
21 | 0.27616 | 0.53 | 512.742 | -337.5 | 4924.7579 |  | 491.0096 | 1391.6632 | 0
22 | 0.27117 | 0.53 | 508.746 | -337.5 | 4753.5119 |  | 296.343 | 1095.3202 | 0
23 | 0.26649 | 0.53 | 510.5492 | -337.5 | 3905.4627 |  | 151.9263 | 943.3939 | 0
24 | 0.26111 | 0.53 | 500.7015 | 212.625 | 3192.1362 |  | 32.0048 | 911.3891 | 0
0

## DAY 51th_ECO_OBJ_BASE3
| ELEC_PRIC | EL | HP | BATT | GRID | THERMAL LOAD | PCM | BOILER | 0.25714 | 0.25443 | 0.25298 | 0.25275 | 0.25498 | 0.20627 | 0.26978 | 0.27708 | 0.27673 | 0.27678 | 0.27037 | 0.2669 | 0.26475 | 0.26649 | 0.27007 | 0.27432 | 0.27111 | 0.28213 | 0.2809 | 0.27616 | 0.27117 | 0.06649 | 0.061108
1 | 0.26039 | 391.7357 | 337.5 | 3200 | 0 | 62.75 | 791.476 | 62.75
2 | 0.25714 | 395.1273 | 337.5 | 4200 | 1732.6273 | 62.75 | 2271.476 | 62.75
3 | 0.25443 | 386.8388 | 337.5 | 5200 | 1724.3388 | 62.75 | 4542.952 | 62.75
4 | 0.25298 | 400.3276 | 337.5 | 6400 | 1937.8276 | 62.75 | 6814.428 | 62.75
5 | 0.25275 | 398.2891 | 337.5 | 6400 | 735.7891 | 62.75 | 7380 | 62.75
6 | 0.25498 | 485.7462 | 337.5 | 6400 | 823.2462 | 89.093 | 7290.907 | 0
7 | 0.26271 | 487.6569 | 337.5 | 6400 | 1648.4031 | 608.3333 | 6682.5737 | 0
8 | 0.26978 | 514.6485 | -337.5 | 5885.3515 | -337.5 | 1032.7789 | 5649.7947 | 0
9 | 0.27708 | 272.8647 | -337.5 | 5612.4868 | -337.5 | 1047.9167 | 4601.8781 | 0
10 | 0.27673 | -477.4913 | -212.625 | 5612.4868 | -264.8663 | 857.7355 | 3744.1425 | 0
11 | 0.27678 | -1103.9603 | 0 | 5612.4868 | -1103.9603 | 744.0641 | 3000.0785 | 0
12 | 0.27037 | -725.2451 | 0 | 5612.4868 | -725.2451 | 763.9758 | 2236.1027 | 0
13 | 0.2669 | -860.6872 | 0 | 5612.4868 | -860.6872 | 718.9807 | 1517.122 | 0
14 | 0.26475 | -423.8448 | 0 | 5612.4868 | -423.8448 | 719.5689 | 797.5531 | 0
15 | 0.26649 | -910.6803 | 0 | 6396 | -125 | 694.4022 | 103.1509 | 0
16 | 0.27007 | -930.26 | 0 | 6396 | -930.26 | 720.157 | 0 | 617
17 | 0.27432 | -999.7032 | 0 | 6396 | -999.7032 | 765.2354 | 1480 | 765.2354
18 | 0.27111 | -114.5188 | 0 | 6396 | -114.5188 | 745.3237 | 2960 | 745.3237
19 | 0.28213 | 337.5168 | -337.5 | 4561 | 1835 | 475.8719 | 2484.1281 | 0
20 | 0.2809 | 465.6 | -337.5 | 4432.9 | 0 | 601.4552 | 1882.6729 | 0
21 | 0.27616 | 512.742 | -337.5 | 4257.6579 | 0 | 491.0096 | 1391.6632 | 0
22 | 0.27117 | 508.746 | -337.5 | 4086.4119 | 0 | 296.343 | 1095.3202 | 0
23 | 0.26649 | 510.5492 | -337.5 | 3913.3627 | 0 | 151.9263 | 943.3939 | 0
24 | 0.26111 | 500.7015 | 212.625 | 3200.0362 | 0 | 32.0048 | 911.3891 | 0
0

## DAY 51th_ECO_OBJ_BASE2
| ELEC_PRIC | PRICE_GAS [c€/m3] | EL | HP | BATT | EL_GRID | THERMAL LOAD | PCM | BOILER | P_battery | P_PCM | El_mismatch | Th Mismatch | 0.25714 | 0.25443 | 0.25298 | 0.25275 | 0.25498 | 0.20627 | 0.26978 | 0.27708 | 0.27673 | 0.27678 | 0.27037 | 0.2669 | 0.26475 | 0.26649 | 0.27007 | 0.27432 | 0.27111 | 0.28213 | 0.2809 | 0.27616 | 0.27117 | 0.06649 | 0.061108
1 | 0.26039 | 0.53 | 391.7357 | 337.5 | 3600 | 0 | 62.75 | 0 | 62.75 | 0 | 0 | 729.2357 | 0
2 | 0.25714 | 0.53 | 395.1273 | 337.5 | 3600 | 0 | 62.75 | 1100 | 62.75 | 0 | 0 | 732.6273 | 0
3 | 0.25443 | 0.53 | 386.8388 | 337.5 | 3600 | 0 | 62.75 | 2200 | 62.75 | 0 | 0 | 724.3388 | 0
4 | 0.25298 | 0.53 | 400.3276 | 337.5 | 3600 | 0 | 62.75 | 3300 | 62.75 | 0 | 0 | 737.8276 | 0
5 | 0.25275 | 0.53 | 398.2891 | 337.5 | 3600 | 0 | 62.75 | 4100 | 62.75 | 0 | 0 | 735.7891 | 0
6 | 0.25498 | 0.53 | 485.7462 | 337.5 | 3600 | 0 | 89.093 | 4100 | 0 | 0 | -62.75 | 823.2462 | -151.843
7 | 0.26271 | 0.53 | 487.6569 | 337.5 | 3600 | 0 | 608.3333 | 3491.6667 | 0 | 0 | 0 | 825.1569 | -608.3333
8 | 0.26978 | 0.53 | 514.6485 | -337.5 | 3600 | 177.1485 | 1032.7789 | 2458.8877 | 0 | 0 | 0 | 354.2971 | -1032.7789
9 | 0.27708 | 0.53 | 272.8647 | -337.5 | 3600 | -64.6353 | 1047.9167 | 1410.971 | 0 | 0 | 0 | -129.2707 | -1047.9167
10 | 0.27673 | 0.53 | -477.4913 | -212.625 | 3600 | -690.1163 | 857.7355 | 553.2355 | 0 | 0 | 0 | -1380.2325 | -857.7355
11 | 0.27678 | 0.53 | -1103.9603 | 0 | 3600 | -1103.9603 | 744.0641 | 0 | 191 | 0 | 191 | -2207.9206 | -362.0641
12 | 0.27037 | 0.53 | -725.2451 | 0 | 3600 | -725.2451 | 763.9758 | 1100 | 763.9758 | 0 | 572.9758 | -1450.4902 | 572.9758
13 | 0.2669 | 0.53 | -860.6872 | 0 | 4460.6872 | 0 | 718.9807 | 2200 | 718.9807 | 860.6872 | -44.995 | 1.1369e-13 | -44.995
14 | 0.26475 | 0.53 | -423.8448 | 0 | 4884.532 | 0 | 719.5689 | 3300 | 719.56 | 423.8448 | 0.57927 | 1.1369e-13 | 0.57039
15 | 0.26649 | 0.53 | -910.6803 | 0 | 5795.2123 | 0 | 694.4022 | 4100 | 694.4 | 910.6803 | -25.16 | -2.2737e-13 | -25.1622
16 | 0.27007 | 0.53 | -930.26 | 0 | 5795.2123 | 0 | 720.157 | 3379.843 | 0 | 0 | -694.4 | -930.26 | -1414.557
17 | 0.27432 | 0.53 | -999.7032 | 0 | 5795.2123 | 0 | 765.2354 | 2614.6076 | 0 | 0 | 0 | -999.7032 | -765.2354
18 | 0.27111 | 0.53 | -114.5188 | 0 | 5909.7311 | 0 | 745.3237 | 1869.2838 | 0 | 114.5188 | 0 | -3.1264e-13 | -745.3237
19 | 0.28213 | 0.53 | 337.5168 | -337.5 | 3909.73 | -2000 | 475.8719 | 1393.4119 | 0 | -2000.0011 | 0 | -3999.9843 | -475.8719
20 | 0.2809 | 0.53 | 465.6 | -337.5 | 3781.63 | 0 | 601.4552 | 791.9567 | 0 | -128.1 | 0 | 5.6843e-14 | -601.4552
21 | 0.27616 | 0.53 | 512.742 | -337.5 | 3606.3879 | 0 | 491.0096 | 300.9471 | 0 | -175.242 | 0 | -1.1369e-13 | -491.0096
22 | 0.27117 | 0.53 | 508.746 | -337.5 | 3606.388 | 171.246 | 296.343 | 0 | 42 | 5.8339e-05 | 42 | 342.4921 | -212.343
23 | 0.26649 | 0.53 | 510.5492 | -337.5 | 3600.23 | 343.0492 | 151.9263 | 0 | 0 | -6.158 | -42 | 509.9404 | -193.9263
24 | 0.26111 | 0.53 | 500.7015 | 212.625 | 3600.23 | 670.9105 | 32.0048 | 0 | 32.0048 | 0 | 32.0048 | 1384.237 | 32.0048
|  |  | 22.6994 | 0 | 97945.183 | -3221.6027 | 11869.9262 | 43764.811 | 3475.6713 | 0.23 | -30.7452

## DAY 51th_SELFCONSUMPTION_BASE2
| PRIC EL | PRICE_GAS [c€/m3] | EL LOAD | HP | BATT | GRID | TH LOAD | PCM | BOILER | 0.25714 | 0.25443 | 0.25298 | 0.25275 | 0.25498 | 0.20627 | 0.26978 | 0.27708 | 0.27673 | 0.27678 | 0.27037 | 0.2669 | 0.26475 | 0.26649 | 0.27007 | 0.27432 | 0.27111 | 0.28213 | 0.2809 | 0.27616 | 0.27117 | 0.06649 | 0.061108
1 | 0.26039 | 0.53 | 391.7357 | 337.5 | 3600 | 0 | 62.75 | 0 | 62.75
2 | 0.25714 | 0.53 | 395.1273 | 337.5 | 2867.3727 | 0 | 62.75 | 1100 | 62.75
3 | 0.25443 | 0.53 | 386.8388 | 337.5 | 2143.0339 | 0 | 62.75 | 2200 | 62.75
4 | 0.25298 | 0.53 | 400.3276 | 337.5 | 1405.2063 | 0 | 62.75 | 3300 | 62.75
5 | 0.25275 | 0.53 | 398.2891 | 337.5 | 669.4173 | 0 | 62.75 | 4100 | 62.75
6 | 0.25498 | 0.53 | 485.7462 | 337.5 | 0 | 153.9 | 89.093 | 4100 | 0
7 | 0.26271 | 0.53 | 487.6569 | 337.5 | 0 | 150.1569 | 608.3333 | 3491.6667 | 0
8 | 0.26978 | 0.53 | 514.6485 | -337.5 | 0 | 177.1485 | 1032.7789 | 2458.8877 | 0
9 | 0.27708 | 0.53 | 272.8647 | -337.5 | 64.63 | 0 | 1047.9167 | 1410.971 | 0
10 | 0.27673 | 0.53 | -477.4913 | -212.625 | 754.7463 | 0 | 857.7355 | 553.2355 | 0
11 | 0.27678 | 0.53 | -1103.9603 | 0 | 1858.7066 | 0 | 744.0641 | 0 | 191
12 | 0.27037 | 0.53 | -725.2451 | 0 | 2583.9517 | 0 | 763.9758 | 1100 | 763.9758
13 | 0.2669 | 0.53 | -860.6872 | 0 | 3444.6388 | 0 | 718.9807 | 2200 | 718.9807
14 | 0.26475 | 0.53 | -423.8448 | 0 | 3868.4836 | 0 | 719.5689 | 3300 | 719.56
15 | 0.26649 | 0.53 | -910.6803 | 0 | 4779.164 | 0 | 694.4022 | 4100 | 694.4
16 | 0.27007 | 0.53 | -930.26 | 0 | 5709.424 | 0 | 720.157 | 3379.843 | 0
17 | 0.27432 | 0.53 | -999.7032 | 0 | 6709.1271 | 0 | 765.2354 | 2614.6076 | 0
18 | 0.27111 | 0.53 | -114.5188 | 0 | 6823.6459 | 0 | 745.3237 | 1869.2838 | 0
19 | 0.28213 | 0.53 | 337.5168 | -337.5 | 4960.9659 | -1862.68 | 475.8719 | 1393.4119 | 0
20 | 0.2809 | 0.53 | 465.6 | -337.5 | 4832.8659 | 0 | 601.4552 | 791.9567 | 0
21 | 0.27616 | 0.53 | 512.742 | -337.5 | 4657.6238 | 0 | 491.0096 | 300.9471 | 0
22 | 0.27117 | 0.53 | 508.746 | -337.5 | 4486.3778 | 0 | 296.343 | 0 | 42
23 | 0.26649 | 0.53 | 510.5492 | -337.5 | 4313.3286 | 0 | 151.9263 | 0 | 0
24 | 0.26111 | 0.53 | 500.7015 | 212.625 | 3600.0021 | 0 | 0 | 0 | 32.0048