## Technology Parameters
| HP | BAT | PCM |  | WG | PV
max kW / module | 50 | 82 | 50 | Capital cost | 2500 | 2000
max kWh (=100%Soc) / module | 286.125 | 82 | 205 | O&M cost Euro/kWh | 0.012 | 0.01
O&M cost/kWh | 0.0011 | 0.002 | 0.003
O&M cost / module | 0.31474 | 0.164 | 0.615
Specific capital cost/kWh | 200 | 350 | 83
Specific capital cost/modul | 57225 | 28700 | 17015
Hipothesys
HP
Plant power: | 450 | kW
Plant efficiency: | 0.75
Pumping power: | 600 | kW
Stored energy: | 2575 | kWh
Discharge time: just over | 5 | hours
Charge time: | 6 | hours
O&M | 11 | c€/kWh
BATTERY
Plant power: | 6806 | kW
Plant efficiency: | over 99%
Stored energy: | 6806 | kWh
Discharge time: just over | 1 | hour
Charge time: | 1 | hour
O&M | 0.2 | c€/kWh
SCENARIO SELF CONSUMPTION |  |  | The self-consumption scenario means that we minimize the energy drawn from the grid. |  |  |  | KPI= | total energy buy fom the grid for the considered scenario (i.e., 51th day)/ total energy bought from the distribution grid scenario base
SCENARIO ECO OBJ |  |  | The eco -bj scenario means that we minimize the total energy costs |  |  |  | KPI = | OBJ FUNCTION VALUE for the considered scenario / OBJ FUNCTION VALUE SCENARIO BASE
Note on C4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: I have changed this values

## Scenario
[5 empty] | Total maximum power |  |  | Total capacity of ESS
| NESS_HP | NESS_BAT | NESS_PCM | Total capital cost of storage | HP (kW) | BAT (kW) | PCM (kW) | HP (kWh) | BAT (kWh) | PCM (kWh) | Total O&M cost of storage
Scenario_Base_1 | 9 | 83 | 28 | 3373545 | 450 | 6806 | 1400 | 2575.125 | 6806 | 5740 | 56.4002 |  | 0.2439 | termico
Scenario_Base_2 | 9 | 88 | 20 | 3380925 | 450 | 7216 | 1000 | 2575.125 | 7216 | 4100 | 53.5303
Scenario_Base_3 | 9 | 78 | 36 | 3366165 | 450 | 6396 | 1800 | 2575.125 | 6396 | 7380 | 59.2703
Scenario_UpperCost_1 | 9 | 90 | 36 | 3710565 | 450 | 7380 | 1800 | 2575.125 | 7380 | 7380 | 64.1903 | 1148
Scenario_UpperCost_2 | 9 | 95 | 28 | 3717945 | 450 | 7790 | 1400 | 2575.125 | 7790 | 5740 | 61.3203
Scenario_UpperCost_3 | 9 | 85 | 44 | 3703185 | 450 | 6970 | 2200 | 2575.125 | 6970 | 9020 | 67.0602
Scenario_LowerCost_1 | 9 | 75 | 22 | 3041855 | 450 | 6150 | 1100 | 2575.125 | 6150 | 4510 | 49.4303
Scenario_LowerCost_2 | 9 | 80 | 13 | 3032220 | 450 | 6560 | 650 | 2575.125 | 6560 | 2665 | 45.9453
Scenario_LowerCost_3 | 9 | 70 | 30 | 3034475 | 450 | 5740 | 1500 | 2575.125 | 5740 | 6150 | 52.3003
Scenario_Base_1 |  | 0 | 0
Scenario_Base_2 |  | 5 | -8
Scenario_Base_3 |  | -5 | 8 | [9 empty] | 2870 | 2837.5
Scenario_UpperCost_1 |  | 7 | 8 | [10 empty] | 709.375
Scenario_UpperCost_2 |  | 12 | 0
Scenario_UpperCost_3 |  | 2 | 16
Scenario_LowerCost_1 |  | -8 | -6
Scenario_LowerCost_2 |  | -3 | -15
Scenario_LowerCost_3 |  | -13 | 2
Same Capital Cost
10% investment increase
10% investment decrease

## DAY 51th_V1
| ELEC_PRIC | EL | HP | SoC_BATT | EL_GRID | PCM e | TOT ELE | P_ Battery | Power mismatch | SoC_HP | SoC_PCMe | PRICE_GAS [c€/m3] | THERMAL LOAD | PCMt | BOILER | Tot Termico | SoC_PCMt | 0.25714 | 0.25443 | 0.25298 | 0.25275 | 0.25498 | 0.20627 | 0.26978 | 0.27708 | 0.27673 | 0.27678 | 0.27037 | 0.2669 | 0.26475 | 0.26649 | 0.27007 | 0.27432 | 0.27111 | 0.28213 | 0.2809 | 0.27616 | 0.27117 | 0.06649 | 0.061108
0
1 | 0.26039 | 391.7357 | 168.75 | 3400 | -2839 | 0 | 0 | -3400 | -0.51427 | 1437.625 | 0 | 0.53 | 62.75 | 62.75 | 0 | 0 | 62.75
2 | 0.25714 | 395.1273 | 337.5 | 0 | -2948.7 | 0 | 0 | 0 | 3681.3273 | 1775.125 | 0 | 0.53 | 62.75 | 62.75 | 0 | 0 | 125.5
3 | 0.25443 | 386.8388 | 337.5 | 0 | 724.3388 | 0 | 0 | 0 | 0 | 2112.625 | 0 | 0.53 | 62.75 | 62.75 | 0 | 0 | 188.25
4 | 0.25298 | 400.3276 | 337.5 | 0 | 737.8276 | 0 | 0 | 0 | 0 | 2450.125 | 0 | 0.53 | 62.75 | 62.75 | 0 | 0 | 251
5 | 0.25275 | 398.2891 | 337.5 | 0 | 735.7891 | 0 | 0 | 0 | 0 | 2787.625 | 0 | 0.53 | 62.75 | 62.75 | 0 | 0 | 313.75
6 | 0.25498 | 485.7462 | 337.5 | 0 | 823.2462 | 0 | 0 | 0 | 0 | 3125.125 | 0 | 0.53 | 89.093 | 89.093 | 0 | 0 | 402.843
7 | 0.26271 | 487.6569 | 337.5 | 0 | 637.2569 | -187.9 | 0 | 0 | 0 | 3462.625 | -187.9 | 0.53 | 608.3333 | 608.3333 | 0 | 0 | 1011.1763
8 | 0.26978 | 514.6485 | -337.5 | 0 | 95.34 | -81.8 | 0 | 142.6 | 142.6085 | 3125.125 | -269.7 | 0.53 | 1032.7789 | 1032.7789 | 0 | 0 | 2043.9553
9 | 0.27708 | 272.8647 | -337.5 | 142.6 | 0 | -78.02 | 0 | 815.6813 | 673.0259 | 2787.625 | -347.72 | 0.53 | 1047.9167 | 1047.9167 | 0 | 0 | 3091.8719
10 | 0.27673 | -477.4913 | -212.625 | 958.2813 | 0 | -125.565 |  | 1257.9353 | 442.254 | 2575 | -473.285 | 0.53 | 857.7355 | 857.7355 | 0 | 0 | 3949.6075
11 | 0.27678 | -1103.9603 | 0 | 2216.2166 | 0 | -153.975 | 0 | 874.2451 | -383.6902 | 2575 | -627.26 | 0.53 | 744.0641 | 744.0641 | 0 | 0 | 4693.6715
12 | 0.27037 | -725.2451 | 0 | 3090.4617 | 0 | -149 | 0 | 1020.9372 | 146.6921 | 2575 | -776.26 | 0.53 | 763.9758 | 763.9758 | 0 | 0 | 5457.6473
13 | 0.2669 | -860.6872 | 0 | 4111.3988 | 0 | -160.25 | 0 | 583.9523 | -436.9848 | 2575 | -936.51 | 0.53 | 718.9807 | 718.9807 | 0 | 0 | 6176.628
14 | 0.26475 | -423.8448 | 0 | 4695.3511 | 0 | -160.1075 | 0 | 1077.0803 | 493.128 | 2575 | -1096.6175 | 0.53 | 719.5689 | 719.5689 | 0 | 0 | 6896.1969
15 | 0.26649 | -910.6803 | 0 | 5772.4315 | 0 | -166.4 | 0 | 1033.5685 | -43.5118 | 2575 | -1263.0175 | 0.53 | 694.4022 | 694.4022 | 0 | 0 | 7590.5991
16 | 0.27007 | -930.26 | 0 | 6806 | -56.59 | -159.9 | 0 | 0 | -1033.57 | 2575 | -1422.9175 | 0.53 | 720.157 | 720.157 | 0 | 0 | 8310.7562
17 | 0.27432 | -999.7032 | 0 | 6806 | -1148.4 | -148.7 | 0 | 0 | -0.0031783 | 2575 | -1571.6175 | 0.53 | 765.2354 | 765.2354 | 0 | 0 | 9075.9916
18 | 0.27111 | -114.5188 | 0 | 6806 | -268.2188 | -153.7 | 0 | -683 | -683 | 2575 | -1725.3175 | 0.53 | 745.3237 | 745.3237 | 0 | 0 | 9821.3153
19 | 0.28213 | 337.5168 | -337.516 | 6123 | -899 | -216 | 0 | -465.6 | 217.4007 | 2237.484 | -1941.3175 | 0.53 | 475.8719 | 475.8719 | 0 | 0 | 10297.1872
20 | 0.2809 | 465.6 | -337.5 | 5657.4 | -737.5 | -400 | 0 | -512.742 | -47.142 | 1899.984 | -2341.3175 | 0.53 | 601.4552 | 601.4552 | 0 | 0 | 10898.6424
21 | 0.27616 | 512.742 | -337.5 | 5144.6579 | -1046.5 | -709 | 0 | -508.746 | 3.996 | 1562.484 | -3050.3175 | 0.53 | 491.0096 | 491.0096 | 0 | 0 | 11389.6521
22 | 0.27117 | 508.746 | -337.5 | 4635.9119 | -1046.5 | -709 | 0 | -510.5492 | -1.8031 | 1224.984 | -3759.3175 | 0.53 | 296.343 | 296.343 | 0 | 0 | 11685.995
23 | 0.26649 | 510.5492 | -337.5 | 4125.3627 | -1046.5 | -709 | 0 | -500.7015 | 9.8477 | 887.484 | -4468.3175 | 0.53 | 151.9263 | 151.9263 | 0 | 0 | 11837.9214
24 | 0.26111 | 500.7015 | 168.75 | 3624.6612 | -371.25 | -540 | 0 | -224.6612 | 276.0403 | 1056.234 | -5008.3175 | 0.53 | 32.0048 | 32.04 | 0 | 0 | 11869.9614
|  |  |  | 3400 |  | -5008.3175 |  | 0